University of Newcastle upon Tyne

School of Civil Engineering & Geosciences

Coursework Task Sheet

Task Reference Number:		CIV911/cw/1

Title:	Drinking Water Treatment Plant Design

Task Description

Design a water treatment plant to provide drinking water for a population of 450,000 people, based on the raw water quality, jar test results and final water quality targets given overleaf, and relevant UK and EU standards.

Report

The report must be typed in 12 point font and be not more than 10 sides of A4 (excluding title page, contents page, references and plant layout diagram).  The report should be bound in School covers and must include:

- Title page and contents page

- Brief details of the design requirements with appropriate comments and assumptions

- Brief description of the overall treatment plant design capacity and layout

- Diagram of the plant layout with labelled unit processes

- Design details of all unit processes, including calculations (include at relevant section, not as appendices)

- Estimation of the size of the main chemical storage units

- Brief description of the assumptions and reasons for the choice and design of each unit process and storage unit

- List of references (cited in the text where relevant)

Submission date:	Monday 25th April 2005

Return date:		Monday 23th May 2005

Assessment:

Coursework contributes 40% to the total assessment for this module.

This item of coursework contributes 25% to the total assessment for the module.

Marking Scheme:

Design (30%), Explanations (30%), Calculations (20%), Presentation (20%)

River water quality

Parameter		Unit			Max		Min		Mean

pH						8.5		6.5		7.8

Colour			Hazen			29		<1		10

Turbidity		NTU			46		<0.1		2.5

Total Iron		g/l			5170		<20		285

Total Manganese	g/l			850		<20		40

Total Aluminium	g/l			2530		<20		122

Alkalinity		mg CaCO3/l		215		41		139

Total Hardness	mg CaCO3/l		263		97		169

TOC			mg/l			10.8		<0.2		4.0

Ammonia		mg NH4/l		2.29		<0.01		0.06

Jar test data

Four concentrations of alum were mixed with samples of raw river water and adjusted to four pH levels to determine the optimal flocculation response.

| Alum addition (mg/l) | Initial pH | Colour (Hazen) | Turbidity (NTU) | Floc Size* | Final pH |
| --- | --- | --- | --- | --- | --- |
| 30 | 6 | 40 | 14 | A | 6 |
| 60 | 6 | 70 | 3.5 | C | 6.15 |
| 90 | 6 | 30 | 1.9 | D | 6.1 |
| 120 | 6 | 40 | 2.4 | C | 6 |
| 30 | 6.5 | 400 | 9.3 | A | 6.39 |
| 60 | 6.5 | 125 | 4.3 | F | 6.41 |
| 90 | 6.5 | 20 | 1 | E | 6.47 |
| 120 | 6.5 | 100 | 2.7 | E | 6.97 |
| 30 | 7 | 500 | 12 | A | 6.59 |
| 60 | 7 | 450 | 15 | A | 6.65 |
| 90 | 7 | 100 | 3.5 | D | 6.55 |
| 120 | 7 | 100 | 3.4 | E | 6.84 |
| 30 | 7.5 | 450 | 9.2 | A | 6.87 |
| 60 | 7.5 | 450 | 16 | A | 7.01 |
| 90 | 7.5 | 200 | 8.5 | G | 7.17 |
| 120 | 7.5 | 125 | 5 | G | 7.61 |

*A indicates small flocs (typical size 0.3-0.5 mm)

G indicates large flocs (typical size 3.0-4.5 mm)

Final water quality targets

Parameter		Unit			Target	Max

Colour			Hazen			4		10

Turbidity		NTU			0.5		1

Total Iron		g/l			50		100

Total Manganese	g/l			20		50

Total Aluminium	g/l			50		100